FRONT-END ENGINEERING DESIGN (FEED)

100 t/d Sulfuric Acid Plant — DCDA / Elemental Sulfur

INSTRUMENT INDEX (II)

ISA-5.1 Tagged — Range vs Operating Envelope Consistency Check

| Attribute | Value |
| --- | --- |
| Document No. | PRJ-SA100-FEED-II-004 |
| Revision | A0 — Issued for Review |
| Project | 100 t/d H₂SO₄ Plant, DCDA Route |
| Date | August 2026 |
| Status | FEED — Consistency-Checked Edition |

# UNIT 100 — SULFUR HANDLING INSTRUMENTS

| Tag | Service | Instrument Range | Normal Op Value | Max Op (Surge) | Alarm HH or LL Setpoint |
| --- | --- | --- | --- | --- | --- |
| FT-101 | Molten Sulfur Flow | 0–2,000 kg/h | 1,363 | 1,499 | FAH 1,700 / FAL 400 |
| TT-101 | Tank Temperature | 0–200°C | 140 | 140 | TAHH 155 / TALL 130 |
| TT-102 | Transfer Line Temp. | 0–250°C | 140 | 142 | TAHH 155 / TALL 130 |
| LT-101 | Tank Level | 0–100% | 50 | 85 | LSHH 92 / LSLL 15 |
| PT-101 | Transfer Line Pressure | 0–10 barg | 0.4 | 0.5 | PAH 2.0 / PAL 0.2 |

# UNIT 200 — FURNACE AND WHB INSTRUMENTS

| Tag | Service | Instrument Range | Normal Op Value | Max Op (Surge) | Alarm / Trip Setpoint |
| --- | --- | --- | --- | --- | --- |
| TT-201 | Furnace Temperature | 500–1,200°C | 1,050 | 1,080 | TSHH 1,150 |
| TT-202 | WHB Outlet Temperature | 300–500°C | 420 | 425 | TAH 445 / TAL 380 |
| PT-201 | Furnace Chamber Pressure | −50 to +500 mbar | −15 | −18 | PAHH +300 / PALL −40 |
| FT-201 | Process Air Flow | 0–15,000 Nm³/h | 8,873 | 9,760 | FAH 12,000 / FAL 3,500 |
| FT-202 | WHB Steam Flow | 0–10,000 kg/h | 7,500 | 8,250 | FAH 9,000 |
| PT-202 | WHB Steam Pressure | 0–50 barg | 40 | 40 | PAHH 46 / PAL 35 |
| LT-201 | WHB Drum Level | 0–100% | 50 | 50 | LSHH 90 / LSLL 20 |
| AT-201 | SO₂ Concentration | 0–15 vol% | 10.5 | 10.5 | AAH 12.0 / AAL 8.5 |
| AT-202 | O₂ Concentration | 0–25 vol% | 10.5 | 10.5 | AAL 8.0 |
| TSHH-201 (SIL) | Furnace T HH ESD | 500–1,200°C | 1,050 | 1,080 | SIL trip 1,150°C |
| PSHH-201 (SIL) | Furnace P HH ESD | −50 to +500 mbar | −15 | −18 | SIL trip +300 mbar |

# UNIT 300 — DRYING SYSTEM INSTRUMENTS

| Tag | Service | Instrument Range | Normal Op Value | Max Op (Surge) | Alarm Setpoint |
| --- | --- | --- | --- | --- | --- |
| AT-301 | Moisture in Process Air | 0–0.5 g/Nm³ | 0.05 | 0.07 | AAH 0.15 |
| LT-301 | DT Acid Sump Level | 0–100% | 50 | 50 | LAL 25 / LAHH 90 |
| TT-301 | DT Acid Temperature | 0–120°C | 65 | 70 | TAH 80 |
| AT-302 | DT H₂SO₄ Concentration | 85–98 wt% | 94.5 | 94.5 | AAL 91 / AAH 97 |

# UNIT 400 — CONVERTER INSTRUMENTS

| Tag | Service | Instrument Range | Normal Op Value | Max Op (Surge) | Alarm / Trip Setpoint | Range Adequate? | SIL Setpoint within 90% Span? |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TT-401 | Conv. Pass 1 Inlet T | 350–500°C | 420 | 420 | TSLL 405 / TAH 450 | Yes | N/A |
| TT-402 (SIL) | Conv. P1 Outlet T | 400–700°C | 600 | 621 | TSHH (SIL1) 620 | Yes | 620 = 73.3% of span — OK |
| TT-403 | Conv. Pass 2 Inlet T | 400–500°C | 440 | 442 | TAH 465 / TSLL 410 | Yes | N/A |
| TT-404 | Conv. Pass 2 Outlet T | 400–600°C | 520 | 526 | TSHH 550 | Yes | 550 = 75% span — OK |
| TT-405 | Conv. Pass 3 Inlet T | 400–500°C | 430 | 432 | TAH 450 / TSLL 410 | Yes | N/A |
| TT-406 | Conv. Pass 3 Outlet T | 400–530°C | 480 | 484 | TSHH 500 | Yes | 500 = 76.9% span — OK |
| TT-407 | Conv. Pass 4 Inlet T | 380–460°C | 415 | 416 | TAH 435 / TSLL 400 | Yes | N/A |
| TT-408 | Conv. Pass 4 Outlet T | 380–460°C | 430 | 432 | TSHH 450 | Yes | TSHH 450 = 87.5% span — OK |
| PT-401 | Converter Inlet Gas P | 0–1.5 barg | 0.08 | 0.10 | PAH 0.5 / PAL 0.02 | Yes; process uses <10% of range — marginal resolution | N/A |
| AT-401 | SO₂ — Converter Inlet | 0–12 vol% | 10.5 | 10.5 | AAH 12.0 | AAH at 100% full scale — FAIL | N/A |
| AT-402 | SO₃ — Post Pass 3 | 0–6 vol% | 4.0 | 4.4 | AAH 5.5 | Yes | N/A |
| AT-403 CEMS | Stack SO₂ | 0–1,000 mg/Nm³ | 250 | 480 | AAH 500 / AAHH 600 | Yes | N/A |

# UNIT 500 — ABSORPTION SYSTEM INSTRUMENTS

| Tag | Service | Instrument Range | Normal Op Value | Max Op (Surge) | Alarm Setpoint |
| --- | --- | --- | --- | --- | --- |
| LT-501 | IPAT Sump Level | 0–100% | 50 | 50 | LAHH 90 / LALL 20 |
| TT-501 | IPAT Inlet Gas Temp | 350–500°C | 420 | 432 | TAH 460 |
| TT-502 | IPAT Acid Temperature | 30–120°C | 65 | 70 | TAH 80 / TAL 40 |
| AT-501 | IPAT H₂SO₄ Concentration | 96–99 wt% | 98.2 | 98.2 | AAL 97.5 / AAH 98.8 |
| LT-502 | FAT Sump Level | 0–100% | 50 | 50 | LAHH 90 / LALL 20 |
| TT-503 | FAT Inlet Gas Temp | 390–460°C | 415 | 420 | TAH 445 |
| AT-502 | FAT H₂SO₄ Concentration | 96–99 wt% | 98.2 | 98.2 | AAL 97.5 / AAH 98.8 |
| FT-501 (SIL) | Dilution Water Flow | 0–500 L/h | 220 | 242 | FALL 50 (SIL 1) |

# UNIT 700 — PRODUCT STORAGE AND ESD INSTRUMENTS

| Tag | Service | Instrument Range | Normal Op Value | Max Op (Surge) | Alarm / Trip Setpoint |
| --- | --- | --- | --- | --- | --- |
| LT-701 | Product Tank Level (process) | 0–100% | 50 | 85 | LAH 80 / LAL 15 |
| LT-702 (SIL) | Product Tank Level ESD | 0–100% | 50 | 85 | LSHH 90 (SIL 2 trip) |
| TT-701 | Product Acid Temperature | 15–60°C | 35 | 38 | TAH 45 / TAL 20 |
| AT-701 | Product Conc. In-line | 96–99.5% | 98.2 | 98.2 | AAL 97.8 / AAH 98.6 |
| FT-701 | Product Dispatch Flow | 0–10,000 kg/h | 4,167 | 5,417 | FAH 8,000 |
| AA-901 (F&G) | Area SO₂ Monitor | 0–50 ppm | 0 | ~2 | AAH 5 ppm / AAHH 25 ppm |